## Sheet1
Commodity | Type | Find Number | System | Specification | ISO Drawing Reference | Description | Size | Function | Manufacturer | Model/Part Number | Code of Construction | Body Material | Temperature Rating | Pressure Rating | Protecting Relief Valve | RV Set Pressure | Notes
GN2 | MV | 5017 | 414000 | 816018 | GN2 Fill | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PT-5915/5910 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 5060 | 440 | Deleted per CCB200
GN2 | MV | 5020 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PT-5911/5913 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 5232 | 3300 | CCB167
GN2 | MV | 5039 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1" MSP | 6 ksi GN2 Vehicle Supply Control Panel Isolation | Tescom | 30-1201-316 | B31.3 | 316 SS | -65 to 165 | 6500 | RV 3007 | 6000
GN2 | FIL | 5040 | 414000 | 816031 | GN2 High Pressure Piping | Filter, In Line | 1" MSP | 6 ksi GN2 Vehicle Supply Control Panel | 3B | P84-16ST-25WE | B31.1 | 17-4PH SS | -320 to 550 | 6000 | RV 3007 | 6000
GN2 | REG | 5043 | 414000 | 816019 | GN2 High Pressure Piping | Regulator | 1" MSP | 3000 psig Regulator for LV PHS Supply | Tescom | 44-7426D36W232 | B31.3 | 303 SS | 0 to 165 | 6000 | RV 3007 | 6000
GN2 | MV | 5044 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5045/PT-5917 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 3007 | 6000 | CCB167
GN2 | PG | 5045 | 414000 | 816033 | GN2 High Pressure Piping | Gage, Pressure | 1/4" MST | 3200 psig LV PHS Supply Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 6000 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 3007 | 6000 | Gauge range 6000 psi
GN2 | RV | 5046 | 414000 | 816020 | GN2 High Pressure Piping | Valve, Relief | 1'', 1500# Flange x 2'', 300# Flange | 3200 psig LV PHS Supply Pressure Relief | Anderson Greenwood | 84316F12/S | ASME Section VIII | SS SA351-CF8M | -65f to 600F | 6170 | RV 5046 | 3400
GN2 | DCVN/O | 5047 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Ball, Discrete | 1" BW to flare | 3000 psig LV PHS Supply Flow Control-Primary | Flowserve | 10-EH4466YTSW-V3-V37-V46 | B16.34 | 316 SS | -50 to 75 | 4500 | RV 5046 | 3300 | CCB119
GN2 | DCVN/O | 5047.2 | 414000 | 816018 | GN2 High Pressure Piping | Actuator |  | Actuator for DCVN/O-5047 | Hytork | XL131SR80 |  | Alum / SS | -4 to 212 | 116 | RV 5046 | 3300
GN2 | DCVN/O | 5047.3 | 414000 | 816018 | GN2 High Pressure Piping | Controller |  | Controller for DCVN/O-5047 | Topworx | DXP-M21GNEB1A21 |  | Aluminum | -58 to 176 |  | RV 5046 | 3300
GN2 | MV | 5048 | 414000 | 816018 | GN2 Fill | Valve, Globe, Manual | 1" MSP | GN2 Vehicle Supply Control Panel, Medium Pressure Supply Line Isolation | Dragon | 818 05 16 KT - 749 | B31.3 | 316 SS | to 200 | 6000 | RV 5007 | 3000 | Deleted per CCB200
GN2 | FIL | 5049 | 414000 | 816031 | GN2 Fill | Filter, In Line | 1" MSP | GN2 Vehicle Supply Control Panel, Medium Pressure Supply Line Filter | 3B | P84-16ST-25WE | B31.1 | 17-4PH SS | -320 to 550 | 6000 | RV 5007 | 3000 | Deleted per CCB200
GN2 | REG | 5050 | 414000 | 816019 | GN2 High Pressure Piping | Regulator | 1/4" MSP | Pilot Regulator for GN2 Vehicle Pre-Start and Engine Cavity Purges | Tescom | 26-1063-34 | B31.3 | 316 SS | -40 to 165 | 10000 | RV 3007 | 6000 | Removed per CCB 219
GN2 | DLREG | 5051 | 414000 | 816019 | GN2 High Pressure Piping | Regulator, Dome | 2" MSP | Regulator for GN2 Vehicle Pre-Start and Engine Cavity Purges | Tescom | 26-1261-3163-083 | B31.3 | 316 SS | -20 to 165 | 6000 | RV 3007 | 6000 | Removed per CCB 219
GN2 | DCVN/C | 5052 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Ball, Discrete | 2" | GN2 Vehicle Pre-Start and Engine Cavity Purges Flow Control | J Flow Controls | 2DM4833FTPBW80-200 | B31.3 | Stainless Steel | -20 to 390 | 3600 | RV 5055 | 3000 | Removed per CCB 219
GN2 | DCVN/C | 5052.2 | 414000 | 816018 | GN2 High Pressure Piping | Actuator |  | Actuator for DCVN/C-5052 | Hytork | XL681SR80 |  | Alum / SS | -4 to 212 | 116 | RV 5055 | 3000 | Removed per CCB 219
GN2 | DCVN/C | 5052.3 | 414000 | 816018 | GN2 High Pressure Piping | Controller |  | Controller for DCVN/C-5052 | Topworx | DXP-M21GNEB1A21 |  | Aluminum | -58 to 176 |  | RV 5055 | 3000 | Removed per CCB 219
GN2 | MV | 5053 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5054/PT-5904 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 5055 | 3000 | CCB167/ Removed per CCB219
GN2 | PG | 5054 | 414000 | 816033 | GN2 High Pressure Piping | Gage, Pressure | 1/4" MST | GN2 Vehicle Pre-Start Engine Purge Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 5000 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 5055 | 3000 | Gauge range 5000 psi/ Removed per CCB219
GN2 | RV | 5055 | 414000 | 816020 | GN2 High Pressure Piping | Valve, Relief | 2 x 3 | GN2 Vehicle Pre-Start Engine Purge Pressure Relief | Anderson Greenwood | 24316J23/S | ASME Section VIII | SS SA351-CF8M | -65 to 300 | 6170 | N/A | 3000 | Removed per CCB 219
GN2 | REG | 5057 | 414000 | 816019 | GN2 Fill | Regulator | 1" MSP | GN2 Engine Cavity Purge Pressure | Tescom | 44-1363-3161-411 | B31.3 | 316 SS | -0 to 165 | 4500 | RV 5007 | 3000 | Deleted per CCB200
GN2 | MV | 5058 | 414000 | 816018 | GN2 Fill | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5059/PT-5906 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 5060 | 440 | Deleted per CCB200
GN2 | PG | 5059 | 414000 | 816033 | GN2 Fill | Gage, Pressure | 1/4" MST | GN2 Engine Cavity Purge Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 800 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 5060 | 440 | Deleted per CCB200
GN2 | RV | 5060 | 414000 | 816020 | GN2 Fill | Valve, Relief | 3/4" x 1" | GN2 Engine Cavity Purge Pressure Relief | Anderson Greenwood | 81SJ68-8 | ASME Section VIII | SS SA351-CF8M | -423 to 500 | 6000 | N/A | 440 | Deleted per CCB200
GN2 | MV | 5061 | 414000 | 816018 | GN2 Fill | Valve, Ball, Manual | 1" BW | GN2 Vehicle Engine Cavity Purge Supply Isolation | Kace | 83-3005SR | B16.34 | CF8M | -30 to 450 | 2000 | RV 5060 | 440 | Deleted per CCB200
GN2 | CKV | 5074 | 414000 | 816018 | GN2 Fill | Valve, Check | 1" MSP | Engine Cavity Purge Back Flow Prevention | Circle Seal | 232T1-16JJ | B31.1 | 316 SS | -20 to 400 | 3000 | RV 5060 | 440 | Deleted per CCB200
GN2 | DCVN/O | 5079 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Ball, Discrete | 1" BW to flare | 3000 psig LV PHS Supply Flow Control-Secondary | Flowserve | 10-EH4466YTSW-V3-V37-V46 | B16.34 | 316 SS | -50 to 75 | 4500 | RV 5232 | 3300 | CCB119
GN2 | DCVN/O | 5079.2 | 414000 | 816018 | GN2 High Pressure Piping | Actuator |  | Actuator for DCVN/O-5079 | Hytork | XL131SR80 |  | Alum / SS | -4 to 212 | 116 | RV 5232 | 3300
GN2 | DCVN/O | 5079.3 | 414000 | 816018 | GN2 High Pressure Piping | Controller |  | Controller for DCVN/O-5079 | Topworx | DXP-M21GNEB1A21 |  | Aluminum | -58 to 176 |  | RV 5232 | 3300
GN2 | MV | 5112 | 414000 | 816018 | GN2 Fill | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5116 | Dragon | 1 3 5 4 T 3 | B31.3 | 316 SS | to 200 | 6000 | RV 5007 | 3000 | Deleted per CCB200
GN2 | PG | 5116 | 414000 | 816033 | GN2 Fill | Gage, Pressure | 1/4" MST | GN2 Vehicle Supply Control Panel Supply Line Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 5000 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 5007 | 3000 | Deleted per CCB200
GN2 | MV | 5119 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5120 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 3007 | 6000 | CCB167/ Deleted per CCB-219
GN2 | PG | 5120 | 414000 | 816033 | GN2 High Pressure Piping | Gage, Pressure | 1/4" MST | GN2 Vehicle Pre-Start and Engine Cavity Purges Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 6000 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 3007 | 6000 | Gauge range 6000 psi/ Deleted per CCB-219
GN2 | MV | 5122 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5123 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 3007 | 6000 | CCB167
GN2 | PG | 5123 | 414000 | 816033 | GN2 High Pressure Piping | Gage, Pressure | 1/4" MST | 6 ksi GN2 Vehicle Supply Control Panel Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 6000 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 3007 | 6000 | Gauge range 6000 psi
GN2 | DCVN/C | 5126 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Ball, Discrete | 1" BW to flare | LV PHS GN2 Vent Control | Flowserve | 10-EH4466YTSW-V3-V37-V46 | B31.3 | Stainless Steel | -20F to 180F | 4500 | RV 5046 | 3300 | CCB119
GN2 | DCVN/C | 5126.2 | 414000 | 816018 | GN2 High Pressure Piping | Actuator |  | Actuator for DCVN/C-5126 | Hytork | XL131SR80 |  | Alum / SS | -4 to 212 | 116 | RV 5046 | 3300
GN2 | DCVN/C | 5126.3 | 414000 | 816018 | GN2 High Pressure Piping | Controller |  | Controller for DCVN/C-5126 | Topworx | DXP-M21GNEB1A21 |  | Aluminum | -58 to 176 |  | RV 5046 | 3300
GN2 | ACC | 5131 | 414000 | 815047 | GN2 High Pressure Piping | GN2 Accumulator | 1" MSP | GN2 Vehicle Pre-Start Engine Purge | QHP | 170-9915 | ASME Section VIII | SA 479 316 SS | -4 to 100 | 3000 | RV 5055 | 3000 | Deleted per CCB-219 (Abandon in place)
GN2 | MV | 5132 | 414000 | 816018 | GN2 Fill | Valve, Ball, Manual | 3/8" MSP | Engine Cavity Purge Line Vent | Dragon | 10F 0 5 6T | B31.3 | 316 SS |  |  | RV 5060 | 440 | Deleted per CCB200
GN2 | MV | 5150 | 414000 |  | GN2 High pressure piping | Valve, GN2 PHS Vent | 1/4 " NPT |  | Dragon | 818 05 4 KT-749 | B31.3 | 316 Stainless Steel |  | 6000 |  |  | CCB107
GN2 | MV | 5151 | 414000 |  | GN2 High pressure piping | Valve, GN2 PHS Vent | 1/4 " NPT |  | Dragon | 818 05 4 KT-749 | B31.3 | 316 Stainless Steel |  | 6000 |  |  | CCB107
GN2 | MV | 5160 | 414000 | 816018 | GN2 Fill | Valve, Globe, Manual | 3/8" MSP | Line Vent for PG-5116 | Dragon | 818 05 6 KT - 749 | B31.3 | 316 SS | to 200 | 6000 | RV 5007 | 3000 | Deleted per CCB200
GN2 | MV | 5165 | 414000 |  |  | Valve, Metering | 1/4" |  | Swagelok | SS-4L2 | B31.3 | 316 SS | -10°F to 400°F |  |  |  | CCB238
GN2 | MV | 5166 | 414000 |  |  | Valve, Metering | 1/4" |  | Swagelok | SS-4L2 | B31.3 | 316 SS | -10°F to 400°F |  |  |  | CCB238
GN2 | DCVN/C | 5178 | 414000 |  |  | Control Valve | 1" Weld |  | Kace | 83-3005SR | B16.34, B16.25, B1.20.1 | CF8M | -30 to 125 | 2000 | RV 5285, RV5282 | 2000, 2000 | CCB200
GN2 | DCVN/O | 5178.1 | 414000 |  |  | Valve Actuator | NA |  | Hytork | XL131SR80 | ISO 5211 | Aluminum body, end caps, and piston, steel thread, pinion and springs | -4 to 212 | 120 | RV5065, RV5320, RV5319, RV5318, RV5307* | 157, 150 | CCB200
GN2 | DCVN/O | 5178.2 | 414000 |  |  | Valve Controller | NA |  | Topworx | DXP-M21GNEB1A21 | UL 508 | Aluminum Body, 304 Stainless Steel shaft, Buna-N o-rings, aluminum spool valve | -4 to 140 | 100 | RV5065, RV5320, RV5319, RV5318, RV5307* | 157, 150 | CCB200
GN2 | DCVN/C | 5179 | 414000 |  |  | Control Valve | 1" Weld |  | Kace | 83-3005SR | B16.34, B16.25, B1.20.1 | CF8M | -30 to 125 | 2000 | RV5285, RV5282 | 2000, 2000 | CCB200
GN2 | DCVN/O | 5179.1 | 414000 |  |  | Valve Actuator | NA |  | Hytork | XL131SR80 | ISO 5211 | Aluminum body, end caps, and piston, steel thread, pinion and springs | -4 to 212 | 120 | RV5065, RV5320, RV5319, RV5318, RV5307* | 157, 150 | CCB200
GN2 | DCVN/O | 5179.2 | 414000 |  |  | Valve Controller | NA |  | Topworx | DXP-M21GNEB1A21 | UL 508 | Aluminum body, end caps, and piston, steel thread, pinion and springs | -250 to 450 | 100 | RV5065, RV5320, RV5319, RV5318, RV5307* | 157, 150 | CCB200
GN2 | MV | 5180 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 3/8" MSP | Line Vent for PG-5123 | Dragon | 818 05 8 KT - 749 | B31.3 | 316 SS | to 200 | 6000 | RV 3007 | 6000
GN2 | MV | 5185 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 3/8" MSP | GN2 Engine Purge/Cavity Purge Supply Line Vent | Dragon | 818 05 8 KT - 749 | B31.3 | 316 SS | to 200 | 6000 | RV 3007 | 6000 | DELETED per CCB-219
GN2 | REG | 5193 | 414000 | 816019 | GN2 High Pressure Piping | Regulator | 1" MSP | 3000 psig Regulator for LV PHS Backup Supply | Tescom | 44-7426D36W232 | B31.3 | 303 SS | 0 to 165 | 6000 | RV 3007 | 6000
GN2 | MV | 5194 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5195 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 3007 | 6000 | CCB167
GN2 | PG | 5195 | 414000 | 816033 | GN2 High Pressure Piping | Gage, Pressure | 1/4" MST | 3200 psig LV PHS Backup Supply Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 6000 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 3007 | 6000 | Gauge range 6000 psi
GN2 | MV | 5196 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Globe, Manual | 3/8" MSP | GN2 Pre-start Engine Purge Line Vent | Dragon | 818 05 6 KT - 749 | B31.3 | 316 SS | to 200 | 6000 | RV 5055 | 3000 | Deleted per CCB-219
GN2 | DCVN/C | 5198 | 414000 | 816018 | GN2 High Pressure Piping | Valve, Ball, Discrete | 1" BW to flare | LV PHS GN2 Vent Control | Flowserve | 10-EH4466YTSW-V3-V37-V46 | B31.3 | Stainless Steel | -20F to 180F | 4500 | RV 5046 | 3300 | CCB 119
GN2 | DCVN/C | 5198.2 | 414000 | 816018 | GN2 High Pressure Piping | Actuator |  | Actuator for DCVN/C-5198 | Hytork | XL131SR80 |  | Alum / SS | -4 to 212 | 116 | RV 5046 | 3300
GN2 | DCVN/C | 5198.3 | 414000 | 816018 | GN2 High Pressure Piping | Controller |  | Controller for DCVN/C-5198 | Topworx | DXP-M21GNEB1A21 |  | Aluminum | -58 to 176 |  | RV 5046 | 3300
GN2 | REG | 5202 | 414000 | 816019 | GN2 Fill | Regulator | 1" MSP | GN2 Backup Engine Cavity Purge Pressure | Tescom | 44-1363-3161-411 | B31.3 | 316 SS | 0 to 165 | 4500 | RV 5007 | 3000 | Deleted per CCB200
GN2 | RV | 5203 | 414000 | 816020 | GN2 Fill | Valve, Relief | 3/4" x 1" | GN2 Backup Engine Cavity Purge Pressure Relief | Anderson Greenwood | 81SJ68-8 | ASME Section VIII | SS SA351-CF8M | -423 to 500 | 6000 | N/A | 440 | Deleted per CCB200
GN2 | MV | 5204 | 414000 | 816018 | GN2 Fill | Valve, Globe, Manual | 1/4" MST | Isolation Valve for PG-5205 | Dragon / Tescom | TPN: 1 3 5 4 T 3 APN: 30-1101-304 | B31.3 | 316 SS | to 200 | 6000 | RV 5203 | 440 | Deleted per CCB200
GN2 | PG | 5205 | 414000 | 816033 | GN2 Fill | Gage, Pressure | 1/4" MST | GN2 Backup Engine Cavity Purge Pressure | Ashcroft | 45-1379-SSHEJLXC4NHSG 800 | B40.100 | 316 SS | -50 to 200 | See Notes | RV 5203 | 440 | Deleted per CCB200
GN2 | CKV | 5206 | 414000 | 816018 | GN2 Fill | Valve, Check | 1" MSP | Backup Engine Cavity Purge Back Flow Prevention | Circle Seal | 232T1-16JJ | B31.1 | 316 SS | -20 to 400 | 3000 | RV 5203 | 440 | Deleted per CCB200
GN2 | OF | 5207 | 414000 | 815119 | GN2 Fill | Orifice, Fitting | 1" MST | GN2 Backup Engine Cavity PurgeFlow Control | Contract | IES Drawing #600018 |  |  |  |  | RV 5060 | 440 | Deleted per CCB200
GN2 | RV | 5232 | 414000 | 816020 | GN2 High Pressure Piping | Valve, Relief | 1'', 1500# Flange x 2'', 300# Flange | 3200 psig LV PHS Backup Supply Pressure Relief | Anderson Greenwood | 84316F12/S | ASME Section VIII | SS SA351-CF8M | -65 to 600F | 6170 | RV 5232 | 3400
GN2 | ACC | 5233 | 414000 | 815047 | GN2 High Pressure Piping | GN2 Accumulator | 1" MSP | GN2 Vehicle Pre-Start Engine Purge | QHP | 170-9915 | ASME Section VIII | SA 479 316 SS | -4 to 100 | 3000 | RV 5055 | 3000 | Deleted per CCB-219 (Abandon in place)
GN2 | ACC | 5234 | 414000 | 815047 | GN2 High Pressure Piping | GN2 Accumulator | 1" MSP | GN2 Vehicle Pre-Start Engine Purge | QHP | 170-9915 | ASME Section VIII | SA 479 316 SS | -4 to 100 | 3000 | RV 5055 | 3000 | Deleted per CCB-219 (Abandon in place)
GN2 | EREG | 5269 | 414000 |  | Heated GN2 Supply | Regulator | 1/2" |  | Tescom | 26-2064T38A47038 | B31.3 | 316SS | -15 to 165 | Inlet 10000, Outlet 2500 | Inlet RV5266, RV5277, RV5220, RV5221, RV5214, RV5215, RV5011, RV5183, RV5500, RV5262/Outlet RV5285 | 6000/2000 | CCB200
GN2 | EREG | 5269.1 | 414000 |  | Heated GN2 Supply | Regulator Controller | 1/4" |  | Tescom | ER3100EI-1 | NEMA 4X, CSA and FM for Class I, Division 1, Groups B, C, and D | Nickel-plated Brass/FKM solenoids, Glass/Ceramic/Silicon/RTV/Nickel sensors, Glass Filled PET manifold, Polyurethane tubing, Brass plug, Silicone/Buna-N/FKM o-rings, Cast Aluminum/Epoxy Polyester Paint housing | -20 to 170 | 120 | RV5065, RV5320, RV5319, RV5318, RV5307* | 157, 150 | CCB200
GN2 | CKV | 5270 | 414000 |  |  | Valve, Check | 1" MSP |  | Circle Seal | H232T1-16JJ | unknown | 316 SS | -20 to 400 | 6000 | RV 5285 | 2000 | CCB200
GN2 | REG | 5271 | 414000 |  |  | Regulator | 1/2" |  | Tescom | 26-2064T38S47238 | B31.3 | 316 SS | -15 to 165 | Inlet 10000, Outlet 2500 | Inlet RV5266, RV5277, RV5220, RV5221, RV5214, RV5215, RV5011, RV5183, RV5500, RV5262/Outlet RV5285 | 6000/2000 | CCB200
GN2 | CKV | 5272 | 414000 |  |  | Valve, Check | 1" MSP |  | Circle Seal | H232T1-16JJ | unknown | 316 SS | -20 to 400 | 6000 | RV 5282 | 2000 | CCB200
GN2 | PT | 5274 | 414000 |  |  | Pressure Transducer | 1/4" MSP |  | Honeywell Sensotec | AP131DN2N5C6J46X (Order Code 060-N394-01) | unknown | 15-5 PH Stainless Steel wetted parts | -20F to 185F | 3000 | RV 5285 | 2000 | CCB200
GN2 | TC | 5275 | 414000 |  |  | Temp Sensor, RTD | 1/4" MST |  | RDF | 22579-1.6 | ASTM E 1137 | 316L SST | -328 to 212 | 6000 | RV 5285, RV5282 | 2000, 2000 | CCB200
GN2 | PT | 5276 | 414000 |  |  | Pressure Transducer | 1/4" MSP |  | Honeywell Sensotec | AP131DN2N5C6J46X (Order Code 060-N394-01) | unknown | 15-5 PH Stainless Steel wetted parts | -20F to 185F | 3000 | RV5285, RV5282 | 2000, 2000 | CCB200
GN2 | PT | 5278 | 414000 |  |  | Pressure Transducer | 1/4" MSP |  | Honeywell Sensotec | AP131DN2N5C6J46X (Order Code 060-N394-01) | unknown | 15-5 PH Stainless Steel wetted parts | -20F to 185F | 3000 | RV 5282 | 2000 | CCB200
GN2 | MV | 5279 | 414000 |  |  | Manual Valve | 1/4" MST |  | Tescom | 30-1101-304 | B31.3 | 316 SS | -40 to 165 | 6000 | RV 5285 | 2000 | CCB200
GN2 | MV | 5280 | 414000 |  |  | Manual Valve | 1/4" MST |  | Tescom | 30-1101-304 | B31.3 | 316 SS | -40 to 165 | 6000 | RV 5282 | 2000 | CCB200
GN2 | PG | 5281 | 414000 |  |  | Gage, Pressure | 1/4" MST |  | Ashcroft | 45-1379-SSHEJLXSGC4NH 3000 | B40.100 | Aluminum case, Glass window, Aluminum dial, 316L tube and socket | -20 to 250 | 3000 | RV 5282 | 2000 | CCB200
GN2 | RV | 5282 | 414000 |  |  | Valve, Relief | 3/4" x 1" |  | Anderson Greenwood | 81SJ68-8 | ASME Section VIII | 316SS | -423 to 500 | 4000 | RV 5282 | 2000 | CCB200
GN2 | MV | 5284 | 414000 |  |  | Vent Valve | 3/8" MSP |  | Tescom | 30-1301-307 | B31.3 | 316 SS | -40 to 165 | 10000 | RV5285, RV5282 | 1500 | CCB200
GN2 | RV | 5285 | 414000 |  |  | Valve, Relief | 3/4" x 1" |  | Anderson Greenwood | 81SJ68-8 | ASME Section VIII | 316 SS | -423 to 500 | 4000 | RV 5285 | 2000 | CCB200
GN2 | MV | 5286 | 414000 |  |  | Manual Valve | 1/4" MST |  | Tescom | 30-1101-304 | B31.3 | 316 SS | -40 to 165 | 6000 | RV5285, RV5282 | 2000, 2000 | CCB200
GN2 | PG | 5287 | 414000 |  |  | Gage, Pressure | 1/4" MST |  | Ashcroft | 45-13179-SSHEJLXSGC4NH 3000 | B40.100 | Aluminum case, Glass window, Aluminum dial, 316L tube and socket | -20 to 250 | 3000 | RV 5285 | 2000 | CCB200
GN2 | RV | 5358 | 414000 |  | GN2 High Pressure piping | Pilot-Op, Modulating, Non-Flowing Pilot | 1" Inlet |  | Anderson Greenwood | 84316F12/S | ANSI/ASME B16.5 | Stainless Steel | -65F to 600F | 6000 | RV 3030 |  | CCB117 added/CCB181 removed
GN2 | MV | 5375 | 414000 | 816018 | GN2 Muscle Components | Valve, Ball, Manual | 1/2" FNPT | Skid Muscle GN2 isolation valve (GN2 panel) | Kace | 55-1003SR | B16.34 | CF8M | -60 to 400 | 1000 | RV 5307 | 150
GN2 | MV | 5376 | 414000 | 816018 | GN2 Muscle Components | Valve, Ball, Manual | 1/2" FNPT | Skid Muscle GN2 isolation valve (Ghe Panel) | Kace | 55-1003SR | B16.34 | CF8M | -60 to 400 | 1000 | RV 5307 | 150
GN2 | MV | 5380 | 414000 | 816018 | GN2 Instrument Purge | Valve, Needle, Manual | 1/4" MST | Panel Purge Flow Control Valve (GN2 panel) | Dragon | 30 5 4 | B31.3 | 316 SS | to 200 | 4500 | RV 5067 | 150
GN2 | MV | 5381 | 414000 | 816018 | GN2 Instrument Purge | Valve, Needle, Manual | 1/4" MST | Panel Purge Flow Control Valve (GHe panel) | Dragon | 30 5 4 | B31.3 | 316 SS | to 200 | 4500 | RV 5067 | 150
GN2 | MV | 5398 | 414000 |  | GN2 Muscle Components | Valve, Needle, Manual | 1/4" | DCVN/O 4061 Muscle Actuation | Swagelok | SS04L2 |  | 316 SS | -10 to 400 | 2000 | RV 5307 | 150 | CCB 015
GN2 | MV | 5399 | 414000 |  | GN2 Muscle Components | Valve, Needle, Manual | 1/4" | DCVN/O 4062 Muscle Actuation | Swagelok | SS04L2 |  | 316 SS | -10 to 400 | 2000 | RV 5307 | 150 | CCB 015
GN2 | MV | 5400 | 414000 |  | GN2 Muscle Components | Valve, Needle, Manual | 1/4" | DCVN/O 5047 Muscle Actuation | Swagelok | SS04L2 |  | 316 SS | -10 to 400 | 2000 | RV 5046 | 3300 | CCB 015
GN2 | MV | 5401 | 414000 |  | GN2 Muscle Components | Valve, Needle, Manual | 1/4" | DCVN/O 5079 Muscle Actuation | Swagelok | SS04L2 |  | 316 SS | -10 to 400 | 2000 | RV 5307 | 150 | CCB 015
GN2 | PT | 5904 | 414000 | 816033 | GN2 High Pressure Piping | Pressure Sensor, Abs | 1/4" MSP | GN2 Vehicle Pre-Start and Engine Cavity Purges Pressure | Honeywell Sensotec | AP131DN2N5C6J46X |  | 17-4PH SS | -20 to 185 | 3000 | RV 5055 | 3000 | DELETED per CCB-219
GN2 | TC | 5905 | 414000 | 816032 | GN2 High Pressure Piping | Temp Sensor, RTD | 1/4" MST | GN2 Vehicle Pre-Start Engine Purge Temperature | RDF | 22579-2.3 |  | 316L SS | -328 to 212 | 6000 | RV 5055 | 3000 | DELETED per CCB-220
GN2 | PT | 5906 | 414000 | 816033 | GN2 Fill | Pressure Sensor, Abs | 1/4" MSP | GN2 Engine Cavity Purge Pressure | Honeywell Sensotec | AP131CR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 500 | RV 5060 | 440 | Deleted per CCB200
GN2 | TC | 5907 | 414000 | 816032 | GN2 Fill | Temp Sensor, RTD | 1/4" MST | GN2 Vehicle Engine Cavity Purge Temperature | RDF | 22579-1.6 |  | 316L SS | -328 to 212 | 6000 | RV 5060 | 440 | Deleted per CCB200
GN2 | PT | 5910 | 414000 | 816033 | GN2 Fill | Pressure Sensor, Abs | 1/4" MSP | GN2 Engine Cavity Purge Line Pressure (secondary) | Honeywell Sensotec | AP131CR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 500 | RV 5060 | 440 | Deleted per CCB200
GN2 | PT | 5911 | 414000 | 816033 | GN2 High Pressure Piping | Pressure Sensor, Abs | 1/4" MSP | GN2 PHS LV Line Pressure (primary) | Honeywell Sensotec | AP131DR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 5000 | RV 5232 | 3300
GN2 | PT | 5913 | 414000 | 816033 | GN2 High Pressure Piping | Pressure Sensor, Abs | 1/4" MSP | GN2 PHS LV Line Pressure (secondary) | Honeywell Sensotec | AP131DR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 5000 | RV 5232 | 3300
GN2 | PT | 5915 | 414000 | 816033 | GN2 Fill | Pressure Sensor, Abs | 1/4" MSP | GN2 Engine Cavity Purge Line Pressure (primary) | Honeywell Sensotec | AP131CR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 500 | RV 5060 | 440 | Deleted per CCB200
GN2 | TC | 5916 | 414000 | 816032 | GN2 High Pressure Piping | Temp Sensor, RTD | 1/4" MST | LV PHS Supply Temp | RDF | 22579-1.6 |  | 316L SS | -328 to 212 | 6000 | RV 5232 | 3300
GN2 | PT | 5917 | 414000 | 816033 | GN2 High Pressure Piping | Pressure Sensor, Abs | 1/4" MSP | LV PHS Supply Pressure | Honeywell Sensotec | AP131DR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 5000 | RV 3007 | 6000
GN2 | PT | 5920 | 414000 | 816033 | GN2 High Pressure Piping | Pressure Sensor, Abs | 1/4" MSP | 6 ksi GN2 Storage Bottle Backup Line Pressure | Honeywell Sensotec | AP131DR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 5000 | RV 3007 | 6000
GN2 | PT | 5921 | 414000 | 816033 | GN2 Fill | Pressure Sensor, Abs | 1/4" MSP | GN2 Backup Engine Cavity Purge Pressure | Honeywell Sensotec | AP131CR2N5C6J46X |  | 17-4PH SS | -20 to 185 | 500 | RV 5203 | 440 | Deleted per CCB200
GN2 | PT | 5925 | 414000 |  | CCB 073 | Pressure Sensor, Abs | 1/4" MSP | Engine Start Purge Line Regulator Pressure | Honeywell Sensotec | AP131DN2N5C6J46X |  | 17-4PH SS | -20 to 185 | 3000 | RV 5055 | 3000 | CCB 073/ DELETED per CCB-219